Maintenance/provision of adequate ventilation

Annex C of PAS 2035 sets out the requirements for the assessment and improvement of ventilation in any dwelling that is subject to retrofit design and installation work. This should be in accordance both with PAS 2035 and with Approved Document F of the Building Regulations.

The Retrofit Designer for each project should use information gathered by the Retrofit Assessor to assess the adequacy of existing ventilation according to certain criteria. Retrofit Assessors are required to identify and assess existing ventilation systems and confirm their suitability as part of a whole-dwelling assessment.

If one or more of the following conditions are present in the dwelling, it is assessed as inadequate and will require improvement.

| Section 1 – Instances of inadequate ventilation that require improvement | Tick if applicable |
| --- | --- |
| There is evidence of condensation and/or mould growth in the dwelling | ☐ |
| There is no ventilation system, or the existing ventilation system is deemed incomplete or not functional (see section 2 for examples of acceptable, complete ventilation systems) - Evidence that a ventilation system is not working properly would be a lack of significant airflow through the extract or supply grilles or fans. This can be measures easily with a simple vane anemometer | ☐ |
| There are not undercuts of 7 600mm² beneath all internal doors, above the floor finish, to allow air to move through the dwelling | ☐ |
| There is no provision for purge ventilation of each habitable room (e.g. by opening windows) | ☐ |

If any one of the following is present in the dwelling, this is deemed as adequate ventilation:

| Section 2 – Acceptable, Complete Ventilation | Tick if present |
| --- | --- |
| An intermittent extract ventilation (IEV) system consisting of correctly sized extract fans in all 'wet' rooms and correctly sized background ventilators to admit fresh external air in all living spaces and bedrooms or; | ☐ |
| A passive stack ventilation (PSV) system consisting of passive stack ventilators serving all 'wet' rooms and correctly sized background ventilators to admit fresh external air in all living spaces and bedrooms or; | ☐ |
| A continuous positive input ventilation (PIV) system that supplies 'fresh' air, combined with correctly sized background ventilators to allow moist stale air to escape in all living spaces and bedrooms; | ☐ |
| A continuous mechanical extract ventilation (MEV) system that extracts moist, stale air from all 'wet' rooms combined with correctly sized background ventilators to admit fresh external air in all living spaces and bedrooms; | ☐ |
| A whole-house supply and extract MVHR system that extracts moist stale air from all wet rooms, supplies fresh external air to all living spaces and bedrooms and has been properly commissioned and balanced. | ☐ |

Note: Wet rooms are classed as kitchens, bathrooms, shower rooms, utility rooms, and WCs without openable windows.

A procedure for correctly sizing background ventilators can be found in Approved Document F.

If the proposed energy efficiency improvement measures are either intended to reduce the air permeability of the building envelope below 5 m³/m²h at 50 Pa or might do so, then existing IEV or PSV as described in Section 2 shall be assessed as inadequate.

Actions to improve adequacy of ventilation:

1. If the only factor rendering the ventilation inadequate is the lack of IEV fans in all wet rooms, by providing such fans, the ventilation can be then deemed as adequate.

2. If the only factor rendering the ventilation inadequate is a lack of background ventilators, by providing these this can then be deemed as adequate.

3. If the only factor rendering the ventilation inadequate is lack of undercuts beneath all internal doors, by providing these undercuts the ventilation can be classed as adequate.

4. If the lack of purge ventilation is the only factor rendering the ventilation inadequate, provision of an opening window in each room can deem the ventilation as adequate.

The Retrofit Design – Upgrading of Ventilation

Where the dwelling in question requires improved ventilation, there must be proposed improvements included in the Retrofit Design (GD F04).

The Retrofit Coordinator is responsible for ensuring that these improvements have been included within the design where the above inadequacies in Section 2 are present within the existing ventilation.

Where any air-tightness measures are proposed, adequate ventilation should also be included.

Air tightness measures include but are not limited to:

- Draught-stripping of existing doors and windows

- Secondary glazing

- Replacement of existing windows and doors

- The provision of a new air barrier layer in the construction or lining of any exposed floor, wall or roof

- Sealing up of existing chimneys and flues

- Replacement of any open-flued heating or hot water appliance with a room-sealed appliance.

If the ventilation is deemed as inadequate and no air tightness measures are proposed for the property, the Retrofit Coordinator should discuss this with the customer and the Retrofit Designer to recommend air tightness measures to be included, and this should also form part of the medium term improvement plan for any projects deemed to be Path B or C.

Due consideration is to be given to building location, local topography, orientation and internal dimensions/layouts to confirm that natural ventilation (IEV or PSV) is effective. If it is not, ventilation should be improved.

Where ventilation is to be upgraded, the minimum acceptable type of ventilation will be:

- Continuous MEV consisting of one or more fans combined with background ventilators

- Continuous whole-dwelling MVHR, or

- Continuous PIV combined with background ventilators.

All of the above should be tested in accordance with the relevant areas of BS 13141 and whichever is chosen, it should be automatically controlled so as to maintain good air quality and avoid wasted energy.

Air permeability of the building envelope should be considered for each property, as after retrofit this may be lower. In all cases where ventilation is upgraded, purge ventilation shall be considered either through openable windows, or mechanically delivered where openable windows are not available.

Technical requirements can be found in Appendix C of PAS 2035, Approved Document F of the Building Regulations and BS 13141. The Retrofit Coordinator is to ensure that any proposed ventilation upgrade is compliant with all aspects of the ventilation guidance issued within these documents and to refer back to the Retrofit Designer with any concerns.

Please ensure that the ventilation system design includes the following:

| Confirmation that the location, configuration and fixing of the system allows them to operate as quietly as possible, using guidance from PAS 2035 Annex C (section C.3.14). | ☐ |
| --- | --- |
| Confirmation that the system is to be installed by operatives holding suitable qualifications identified in the Register of Regulated Qualifications and approved by the manufacturer or supplier of the system | ☐ |
| Where any new or upgraded ventilation system is proposed as part of a retrofit project, the system design shall include calculation prepared by a technical consultant, specialist designer or the system supplier. | ☐ |

| Project Reference: |  |
| --- | --- |
| Retrofit Coordinator: |  |
| Signed: |  |
| Name of Retrofit Designer: |  |
| Date: |  |